## Summary
LIMPOPO DEPARTMENT OF AGRICULTURE AND RURAL DEVELOPMENT
TOWOOMBA ELECTRICAL WORKS BOQ SUMMARY
ITEM | DESCRIPTION | AMOUNT
NO.
1 | Preliminary and General
2 | Dayworks
3 | Power Generation
SUB-TOTAL
ADD 15% CONTINGENCIES
SUB-TOTAL
ADD 15% VAT
TOTAL BID OFFER

## 1.PnG
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | SECTION A1
1.1 | Preliminaries & General
1,1,1 | Contractual Obligations | Sum | 1
1,1,2 | Works Insurance | Sum | 1
1,1,3 | Setting out of Works | Sum | 1
1,1,4 | Security and Protection of Works | Sum | 1
1,1,5 | Management of Contract | Sum | 1
1,1,6 | Progress Meetings | Sum | 1
1,1,7 | Plant, equipment, sheds & office (min 16m2) | Sum | 1
1,1,8 | Main Notice Board | Sum | 1
1,1,9 | Construction and safety notices boards | Sum | 1
1,1,10 | Water provision | Sum | 1
1,1,11 | Electricity provision | Sum | 1
1,1,12 | Communications | Sum | 1
1,1,13 | Staff housing | Sum | 1
1,1,14 | Ablution facilities | Sum | 1
| Sub-Total A1 (must not exceed 5% of the Bid Amount) |  |  | Sub-Total A1
1.2 | HEALTH AND SAFETY
General:
1,2,1 | Preparation of Contractor's site specific Health and Safety Plan. | Item | 1
1,2,2 | Submission of the Health and Safety File. | Item | 1
1,2,3 | Provision of full time Health and Safety Officer for the entire construction period. | Month | 5
1,2,4 | Induction training of all site personnel throughout construction | No | 1
1,2,5 | Provision of fully equipped/furnished first aid box on site | No | 1
1,2,6 | SANS approved weld mesh type temporary barrier fencing 1,8m high covered with a net fixed to and including 100mm diameter gum poles set securely min 300mm deep in ground at max 3m spacing including excavation, backfilling, etc | m | 200
1,2,7 | Extra over mesh fence for pedestrian gate size 1.8 x 1,8m high. | No | 1
1,2,8 | Provision for Personal Protective Equipment and Protective Clothing per each person: | Prov Sum | 1 | 20000 | 20000
1,2,9 | Mark up for the provision above | % | 20000
Costs of Medical Certificates and Medical Surveillance:
1,2,10 | Entry medical fitness examinations per employee | No | 6
1,2,11 | Respiritory prevention kit allocation and routine screening | No | 6
1,2,12 | Exit Examinations per employee | No | 6
Dust Suppression:
1,2,13 | Dust suppression by spraying construction site or access route with raw water | Cubes | 10
C16. Covid-19 or respiratory or any pandemic outbreak Compliance Measures
1,2,14 | The Contractor is required to price for Covid 19 compliance and the pricing thereof shall be deemed to include all the mandatory requirements. | Sum | 1
Sub-Total A2
1.3 | TIME RELATED CLAIMS
1,3,1 | Claim as per Order Sub-Total Amount before Contingencies and VAT, Max of 5% of the Bid Amount | Sum | 1
1,3,2 | Provision and Payment of CLO | Prov Sum | 5 | 6000 | 30000
1,3,3 | Profit over/Mark-up | % | 30000
Sub-Total A3
Carry to Summary |  |  |  | Sub-Total 1

## 2. Dayworks
ITEM | DAYWORKS ITEMS | UNIT | QTY | RATE | AMOUNT
NO.
2.1 | Contractor's Representative | h | 1 |  | Rate Only
2.2 | Surveyor, working tools included | h | 1 |  | Rate Only
2.3 | Qualified Artisan , tools of trade included
2,3,1 | (i) Plumber | h | 1 |  | Rate Only
2,3,2 | (ii) Boilermaker | h | 1 |  | Rate Only
2,3,3 | (iii) Bricklayer | h | 1 |  | Rate Only
2,3,4 | (iv) Plasterer | h | 1 |  | Rate Only
2,3,5 | (v) Welder with API 1104 Certificate | h | 1 |  | Rate Only
2,3,6 | (vi) Electrician | h | 1 |  | Rate Only
2,3,7 | Foreman, leader-hand | h | 1 |  | Rate Only
2,3,8 | Semi-skilled labourer | h | 1 |  | Rate Only
2,3,9 | General Labourer | h | 1 |  | Rate Only
2.4 | Plant and Equipment
2,4,1 | 8 kVA (petrol power generator) 220V with fuel | h | 1 |  | Rate Only
2,4,2 | 30 kVA (diesel) 380V - 3ph with fuel | h | 1 |  | Rate Only
2,4,3 | 55 kVA (diesel) 380V - 3ph with fuel | h | 1 |  | Rate Only
2,4,4 | TLB Provision (with Fuel and Operator) | h | 1 |  | Rate Only
2,4,5 | Excavator Provision (with Fuel and Operator) | h | 1 |  | Rate Only
2,4,6 | Lowbed Transport , all costs included | km | 1 |  | Rate Only
2,4,7 | 8 Ton Truck Transport , all costs included | km | 1 |  | Rate Only
2,4,8 | LDV transport , all costs included | km | 1 |  | Rate Only
2,4,9 | Water provision, Class 1 quality on 5000 L tanker | sum | 1 |  | Rate Only
2,4,10 | Water provision, Raw water quality on 5000 L tanker for pumping into storage or dust supression | sum | 1 |  | Rate Only
2,5,1 | Provisonal sum for provision of tools and equipment | Prov Sum | 1 | 100000 | 100000
2,5,2 | Profit over above, max 15% | % | 100000
| Carry to Summary |  | SUB TOTAL 2

## 3. Power
| CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 3 : POWER GENERATION EQUIPMNET
3.1 |  | SITE CLEARANCE AND EXCAVATIONS
3.1.1 |  | Clear vegetation and trees of girth up to 1.0 m | m | 100
3.1.2 |  | Clear trees of girth over 1.0 m | No | 10
3.1.3 |  | Excavation for the cabling trench, for soft to intermediate soil | m3 | 130
3.1.4 |  | Extra for Hard rock excavation | m3 | 26
3.2 |  | SOLAR SYSTEM
3.2.1 |  | Supply deliver and install 550-600W monocrystalline or similar solar panels, complete with Ground mounting system including the structure, foundations, installations, corrosion protection,foundations, anchoring, bracings and all necessary accessories. | no | 150
3.2.2 |  | 50 kVA, 3-phase online double-conversion UPS, pure sine-wave output, complete with: * AC input and battery/DC compatibility; * Online double-conversion topology; * 50 kVA / minimum 40 kW output capacity; * 3-phase, 4-wire input and output, 400 V AC, 50 Hz; * Automatic static bypass and manual maintenance bypass; * Automatic transfer to battery operation with zero-break interruption; * Input and output overvoltage and undervoltage protection; * Overload, short-circuit and overcurrent protection; * Overtemperature protection; * Battery deep-discharge protection; * Battery overcharge protection; * Automatic battery charging and battery management; * LED digital display for voltage, current, frequency, load, battery status, alarms and operating mode; * Operating history/event log memory; * Emergency Power Off (EPO) facility; * Audible and visual alarms; * Communication interface for remote monitoring; * Detachable/remote control panel where applicable; * Minimum IP66 enclosure; * Complete with installation, testing and commissioning. | sum | 1
3.2.3 |  | Supply, delivery, installation, testing and commissioning of 100 kWh Lithium Iron Phosphate (LiFePO₄) Battery Energy Storage System (BESS), complete with integrated BMS, protection, monitoring and all accessories, suitable for integration with the solar PV system. | No | 6
3.2.4 |  | Provision for the cabling, protection, isolators, terminals and accessories for the connection of the solar system to the DB. | Prov Sum | 1 | 50000 | 50000
3.2.5 |  | Mark up for the item above | % | 50000
3.2.6 |  | Supply and install DC Cicuit breakers and surge protector | sum | 1
3.2.7 |  | Supply and install Combined Junction Box for solar panels | sum | 1
3.2.8 |  | All-in-one integrated solar LED streetlight, nominal LED power 100 W, minimum luminous flux 18,000 lm, high-efficiency LED ≥180 lm/W, monocrystalline PV module minimum 140 W, LiFePO₄ battery with minimum usable energy capacity of approximately 750 Wh, MPPT charge controller, minimum 12-hour nightly operation and minimum 3-night autonomy under specified operating conditions. Luminaire shall have automatic dusk-to-dawn operation, programmable dimming and optional motion detection. Minimum IP66 protection for the luminaire assembly and corrosion-resistant aluminium housing. Erected on an 8 m hot-dip galvanized tapered steel pole, approximately 3–4 mm wall thickness, with a 76 mm top spigot, subject to the selected luminaire. | sum | 10
3.3 |  | FUEL GENERATORS
3.3.1 |  | Site preparation for the concrete plinth, including removal of the topsoil or cutting out as instructed by the Engineer | m3 | 4
3.3.2 |  | Importing of G5 material and compacting in 150mm layers, to 93% MOD AASHTO for the concrete plinth | m3 | 4
3.3.3 |  | 30MPa Concrete Platform for the Diesel Generator and for post anchoring | m3 | 10
3.3.4 |  | Y16 Reinforcement bars for the Concrete platforms as specified by the Engineer | ton | 0.2
3.3.5 |  | Supply, delivery, installation and commissioning of a 100kVA, 3Phase diesel generator complete with: *Electric start *Automatic voltage regulator and Dashboard dispaly *Automatic transfer switch *Cable connection from the generator to the main DB | sum | 1
3.3.6 |  | Provision of diesel for testing and commissioning of the diesel generator | Litre | 200
3.4 |  | Power Transformers
3.4.1 |  | Allow a sum for replacement, upgrade and installation of power grid transfomers by an Eskom registered contractor as per the Engineer's Instruction, complete with: * Cabling from the transformer to the building; * connections to the existing DB, including upgrading the DB where neccessary; * Upgrading of the overhead cables from the Master Transformer to Workshop transformer; | Prov Sum | 1 | 1600000 | 1600000
3.4.2 |  | Profit over above | % | 1600000
TOTAL SECTION 3 CARRIED FORWARD TO SUMMARY